## COVER
WATER SUPPLY PIPE SIZING TOOL
Hazen-Williams · HDPE PE100 DIN 8074 (Gentex) · Uganda Water Supply Design Manual – 2nd Edition
PROJECT INFORMATION
Project Title
Project Location
Designed By
Checked By
Client / Owner
Contract No.
Date | 02-May-2026
Revision | Rev 0
DESIGN SUMMARY (auto-populated from calculation sheets)
Description | Value | Unit | Source Sheet
Total Dynamic Head (TDH) |  | m | TDH_CALC
Design Flow Rate |  | L/s | TDH_CALC
Estimated Motor Power Required |  | kW | TDH_CALC
Transmission Main — Total Length |  | m | TRANSMISSION
Distribution Network — Total Length |  | m | DISTRIBUTION
CELL COLOUR CODING
Input Cell (yellow bg, dark-blue text) | Enter data here
Formula / Calculated (black text) | Do not edit — auto-calculated
Cross-sheet Link (green text) | References another sheet
✓ OK — within design limits | Velocity and pressure acceptable
⚠ Warning / Out of Range | Action required — revise design
WORKSHEET GUIDE
Sheet | Purpose | Instructions
PARAMETERS | Design constants — H-W C, velocities, pressure ratings, demand factors | Review and adjust defaults before running calculations
PIPE_DB | Full HDPE PE100 catalog (Gentex DIN 8074) — 74 entries OD 20–450 mm | Do NOT modify — auto-referenced by all formulas
TDH_CALC | Total Dynamic Head: production well → storage reservoir; pump sizing | Step 1 — enter well & reservoir survey data
TRANSMISSION | Transmission main — auto OD & PN selection, HGL profile, status checks | Step 2 — enter segment lengths & elevations
DISTRIBUTION | Distribution network — demand calc, branch sizing, node pressure checks | Step 3 — enter branch data; link HGL Start to junction nodes

## PARAMETERS
DESIGN PARAMETERS
# | Parameter | Value | Unit | Reference / Notes
HYDRAULIC PARAMETERS
1 | Hazen-Williams Coefficient C (HDPE PE100) | 150 | - | DIN 8074; Uganda WSS DM Sect 4.3
2 | Min. Flow Velocity — Transmission Main | 0.5 | m/s | Sedimentation prevention; Uganda WSS DM
3 | Max. Flow Velocity — Transmission Main | 2.5 | m/s | Erosion / surge limit for HDPE
4 | Min. Flow Velocity — Distribution | 0.3 | m/s | Sedimentation prevention; Uganda WSS DM
5 | Max. Flow Velocity — Distribution | 1.5 | m/s | Erosion limit; Uganda WSS DM
6 | Minor Loss Factor k (fraction of friction loss) | 0.05 | - | Typical for well-aligned mains; adjust per design
PRESSURE RATINGS — HDPE PE100 DIN 8074 (PE100 compound)
7 | PN-6 Max. Working Head | 61.2 | m | 6 bar → 61.2 m H₂O (design limit = PN head ÷ SF)
8 | PN-10 Max. Working Head | 102 | m | 10 bar → 102.0 m H₂O
9 | PN-16 Max. Working Head | 163.2 | m | 16 bar → 163.2 m H₂O
10 | PN-20 Max. Working Head | 204 | m | 20 bar → 204.0 m H₂O
11 | Pressure Safety Factor | 1.25 | - | Design working head = PN head ÷ SF
DESIGN STANDARDS — Uganda Water Supply Design Manual, 2nd Edition
12 | Min. Residual Pressure — Distribution Consumer | 7 | m | Rural WSS; Uganda WSS DM Sect 5
13 | Min. Residual Pressure — Reservoir / Trans. End | 2 | m | Above reservoir HWL at delivery point
14 | Allowable Head Loss Gradient — Transmission | 5 | m/km | Economic gradient; Uganda WSS DM
15 | Allowable Head Loss Gradient — Distribution | 8 | m/km | Economic gradient; Uganda WSS DM
16 | Pump Design Operating Hours per Day | 8 | hr/day | Uganda WSS DM rural standard
DEMAND PARAMETERS
17 | Per Capita Demand | 20 | L/cap/day | Uganda rural WSS standard; adjust to local survey
18 | Peak Hour Factor (PHF) | 2 | - | Ratio of peak hour to average hourly demand
19 | Peak Day Factor (PDF) | 1.5 | - | Ratio of peak day to average daily demand
20 | NRW / Loss Factor | 1.2 | - | 20% non-revenue water allowance
21 | Population Growth Rate | 0.03 | /yr | 3% per year; verify against census data
22 | Design Period | 20 | years | Standard for Uganda rural water supply projects

## PIPE_DB
HDPE PE100 PIPE CATALOG — DIN 8074 ¦ Gentex
Source: Gentex HDPE Pipes – PE 100 – DIN 8074 Price List (effective July 6, 2018) ¦ OD 20–90mm: 100m rolls ¦ OD 110mm: 50m rolls ¦ OD ≥125mm: 6m or 12m lengths
Item Code | OD (mm) | PN Rating | PN (Numeric) | Internal Dia. ID (mm) | Wall Thickness (mm) | Weight (kg/m) | Price (UGX/m) | Supply Form
5001 | 20 | PN - 6 | 6 | 16.4 | 1.8 | 0.1 | 1400 | 100m roll
5002 | 20 | PN - 10 | 10 | 16.2 | 1.9 | 0.11 | 1500 | 100m roll
5003 | 20 | PN - 16 | 16 | 16.2 | 1.9 | 0.116 | 1700 | 100m roll
5011 | 25 | PN - 6 | 6 | 21.4 | 1.8 | 0.127 | 1800 | 100m roll
5012 | 25 | PN - 10 | 10 | 20.4 | 2.3 | 0.165 | 2400 | 100m roll
5013 | 25 | PN - 16 | 16 | 20.4 | 2.3 | 0.186 | 2700 | 100m roll
5022 | 32 | PN - 6 | 6 | 28.2 | 1.9 | 0.18 | 2600 | 100m roll
5023 | 32 | PN - 10 | 10 | 26.6 | 2.7 | 0.255 | 3600 | 100m roll
5024 | 32 | PN - 16 | 16 | 26.2 | 2.9 | 0.286 | 4000 | 100m roll
5032 | 40 | PN - 6 | 6 | 35.4 | 2.3 | 0.26 | 3800 | 100m roll
5033 | 40 | PN - 10 | 10 | 34.6 | 2.7 | 0.336 | 4900 | 100m roll
5034 | 40 | PN - 16 | 16 | 32.6 | 3.7 | 0.44 | 6300 | 100m roll
5042 | 50 | PN - 6 | 6 | 44.2 | 2.9 | 0.43 | 6100 | 100m roll
5043 | 50 | PN - 10 | 10 | 43.4 | 3.3 | 0.495 | 7100 | 100m roll
5044 | 50 | PN - 16 | 16 | 40.8 | 4.6 | 0.69 | 9600 | 100m roll
5052 | 63 | PN - 6 | 6 | 55.8 | 3.6 | 0.65 | 9200 | 100m roll
5053 | 63 | PN - 10 | 10 | 54.64 | 4.18 | 0.81 | 10700 | 100m roll
5054 | 63 | PN - 16 | 16 | 51.4 | 5.8 | 1.07 | 13400 | 100m roll
5062 | 75 | PN - 6 | 6 | 66.4 | 4.3 | 0.95 | 12600 | 100m roll
5063 | 75 | PN - 10 | 10 | 66 | 4.5 | 1.05 | 13400 | 100m roll
5064 | 75 | PN - 16 | 16 | 61.4 | 6.8 | 1.5 | 20600 | 100m roll
5072 | 90 | PN - 6 | 6 | 79.8 | 5.1 | 1.3 | 16700 | 100m roll
5073 | 90 | PN - 10 | 10 | 79.2 | 5.4 | 1.5 | 19300 | 100m roll
5074 | 90 | PN - 16 | 16 | 73.6 | 8.2 | 2.2 | 30100 | 100m roll
5082 | 110 | PN - 6 | 6 | 97.4 | 6.3 | 1.94 | 24800 | 50m roll
5083 | 110 | PN - 10 | 10 | 96.8 | 6.6 | 2.25 | 28900 | 50m roll
5084 | 110 | PN - 16 | 16 | 90 | 10 | 3.25 | 44600 | 50m roll
5200 | 125 | PN - 6 | 6 | 110.8 | 7.1 | 1.94 | 29300 | 6m / 12m lengths
5237 | 125 | PN - 10 | 10 | 110.2 | 7.4 | 2.9 | 43700 | 6m / 12m lengths
5236 | 125 | PN - 16 | 16 | 102.2 | 11.4 | 4.27 | 64200 | 6m / 12m lengths
5238 | 125 | PN - 20 | 20 | 97 | 14 | 5.12 | 77000 | 6m / 12m lengths
5210 | 140 | PN - 6 | 6 | 124 | 8 | 2.44 | 36800 | 6m / 12m lengths
5241 | 140 | PN - 10 | 10 | 123.4 | 8.3 | 3.64 | 54700 | 6m / 12m lengths
5242 | 140 | PN - 16 | 16 | 114.6 | 12.7 | 5.34 | 80300 | 6m / 12m lengths
5243 | 140 | PN - 20 | 20 | 108.6 | 15.7 | 6.43 | 96700 | 6m / 12m lengths
5092 | 160 | PN - 6 | 6 | 141.8 | 9.1 | 3.2 | 48800 | 6m / 12m lengths
5093 | 160 | PN - 10 | 10 | 141 | 9.5 | 4.9 | 73800 | 6m / 12m lengths
5094 | 160 | PN - 16 | 16 | 130.8 | 14.6 | 7 | 105100 | 6m / 12m lengths
5095 | 160 | PN - 20 | 20 | 124.2 | 17.9 | 8.39 | 125900 | 6m / 12m lengths
5220 | 180 | PN - 6 | 6 | 159.6 | 10.2 | 4 |  | 6m / 12m lengths
5249 | 180 | PN - 10 | 10 | 158.6 | 10.7 | 6 |  | 6m / 12m lengths
5250 | 180 | PN - 16 | 16 | 147.2 | 16.4 | 8.83 |  | 6m / 12m lengths
5251 | 180 | PN - 20 | 20 | 139.8 | 20.1 | 10.6 |  | 6m / 12m lengths
5230 | 200 | PN - 06 | 6 | 185.6 | 7.2 | 4.6 |  | 6m / 12m lengths
5253 | 200 | PN - 10 | 10 | 176.2 | 11.9 | 7.39 |  | 6m / 12m lengths
5254 | 200 | PN - 16 | 16 | 163.6 | 18.2 | 10.9 |  | 6m / 12m lengths
5255 | 200 | PN - 20 | 20 | 155.2 | 22.4 | 13.12 |  | 6m / 12m lengths
5240 | 225 | PN - 06 | 6 | 208.6 | 8.2 | 5.83 |  | 6m / 12m lengths
5257 | 225 | PN - 10 | 10 | 198.2 | 13.4 | 9.38 |  | 6m / 12m lengths
5258 | 225 | PN - 16 | 16 | 184 | 20.5 | 13.79 |  | 6m / 12m lengths
5259 | 225 | PN - 20 | 20 | 174.6 | 25.2 | 16.6 |  | 6m / 12m lengths
5264 | 250 | PN - 06 | 6 | 231.8 | 9.1 | 7.2 |  | 6m / 12m lengths
5261 | 250 | PN - 10 | 10 | 220.4 | 14.8 | 11.48 |  | 6m / 12m lengths
5262 | 250 | PN - 16 | 16 | 204.6 | 22.7 | 17.03 |  | 6m / 12m lengths
5263 | 250 | PN - 20 | 20 | 194.2 | 27.9 | 20.43 |  | 6m / 12m lengths
5260 | 280 | PN - 06 | 6 | 259.8 | 10.1 | 9.03 |  | 6m / 12m lengths
5265 | 280 | PN - 10 | 10 | 246.8 | 16.6 | 14.43 |  | 6m / 12m lengths
5266 | 280 | PN - 16 | 16 | 229.2 | 25.4 | 21.32 |  | 6m / 12m lengths
5267 | 280 | PN - 20 | 20 | 217.4 | 31.3 | 25.66 |  | 6m / 12m lengths
5370 | 315 | PN - 06 | 6 | 292.2 | 11.4 | 11.42 |  | 6m / 12m lengths
5269 | 315 | PN - 10 | 10 | 277.6 | 18.7 | 18.27 |  | 6m / 12m lengths
5270 | 315 | PN - 16 | 16 | 257.8 | 28.6 | 27.05 |  | 6m / 12m lengths
5271 | 315 | PN - 20 | 20 | 244.6 | 35.2 | 32.47 |  | 6m / 12m lengths
5280 | 355 | PN - 06 | 6 | 329.2 | 12.9 | 14.51 |  | 6m / 12m lengths
5273 | 355 | PN - 10 | 10 | 312.8 | 21.1 | 23.26 |  | 6m / 12m lengths
5274 | 355 | PN - 16 | 16 | 290.6 | 32.2 | 34.27 |  | 6m / 12m lengths
5275 | 355 | PN - 20 | 20 | 275.6 | 39.7 | 41.27 |  | 6m / 12m lengths
5290 | 400 | PN - 06 | 6 | 371 | 14.5 | 18.42 |  | 6m / 12m lengths
5277 | 400 | PN - 10 | 10 | 352.6 | 23.7 | 29.4 |  | 6m / 12m lengths
5278 | 400 | PN - 16 | 16 | 327.4 | 36.3 | 43.53 |  | 6m / 12m lengths
5279 | 400 | PN - 20 | 20 | 310.6 | 44.7 | 52.36 |  | 6m / 12m lengths
5300 | 450 | PN - 06 | 6 | 417.4 | 16.3 | 23.31 |  | 6m / 12m lengths
5281 | 450 | PN - 10 | 10 | 396.6 | 26.7 | 37.26 |  | 6m / 12m lengths
5282 | 450 | PN - 16 | 16 | 368.2 | 40.9 | 55.17 |  | 6m / 12m lengths

## TDH_CALC
TOTAL DYNAMIC HEAD (TDH) CALCULATION
Production Well → Storage Reservoir ¦ Hazen-Williams ¦ HDPE PE100 ¦ Uganda WSS DM 2nd Ed.
SECTION 1 — SITE & WELL DATA (enter survey / pump test data)
Ground Elevation at Wellhead |  |  |  |  | m ASL | From topographic survey
Static Water Level (SWL) |  |  |  |  | m bgl | Measured with pump off
Pumping / Dynamic Water Level (PWL) |  |  |  |  | m bgl | From pump test at design flow
Pump Setting Depth |  |  |  |  | m bgl | Depth of pump intake below ground surface
Design Flow Rate Q |  |  |  |  | L/s | Pump design capacity
Pump Operating Hours per Day |  |  |  |  | hr/day | From PARAMETERS — adjust if needed
Reservoir Floor Elevation |  |  |  |  | m ASL | From topographic survey
Reservoir High Water Level (HWL) |  |  |  |  | m ASL | Full storage level
Required Minimum Water Level in Reservoir |  |  |  |  | m ASL | Floor elevation + minimum operational storage depth
SECTION 2 — DERIVED ELEVATIONS
Elevation of Pumping Water Level |  |  |  |  | m ASL
Elevation of Static Water Level |  |  |  |  | m ASL
Minimum Static Head Required (HWL – Pumping WL Elevation) |  |  |  |  | m
SECTION 3 — RISING MAIN / DISCHARGE PIPELINE SEGMENTS
Enter each segment from pump level to reservoir. Segment 1 = pump column (From Elev = Ground Elev – Pump Setting Depth; To Elev = Ground Elev at wellhead). Subsequent segments = surface pipeline to reservoir. Allow. S (col H) defaults to transmission standard — override per segment if needed. OD, PN Rating, and ID are auto-selected from PIPE_DB. Rows with Length = 0 are skipped.
# | Segment Description | Length (m) | From Elev (m ASL) | To Elev (m ASL) | ΔElev (m) | Q (L/s) | Allow. S (m/km) | Min D_req (mm) | Auto OD (mm) | Auto PN Num | Auto PN Rating | Actual ID (mm) | Velocity (m/s) | Friction hf (m) | Minor Loss (m) | Total Loss (m) | Max Press. In Seg (m) | Status
1 | Pump Column (inside well casing) |  |  |  |  | $E$9
2 | Surface Rising Main — Segment 1 |  |  |  |  | $E$9
3 | Surface Rising Main — Segment 2 |  |  |  |  | $E$9
4 | Surface Rising Main — Segment 3 |  |  |  |  | $E$9
5 | [5 empty] | $E$9
6 | [5 empty] | $E$9
7 | [5 empty] | $E$9
8 | [5 empty] | $E$9
9 | [5 empty] | $E$9
10 | [5 empty] | $E$9
11 | [5 empty] | $E$9
12 | [5 empty] | $E$9
TOTALS
SECTION 4 — TOTAL DYNAMIC HEAD SUMMARY
1. Static Head (Reservoir HWL – Pumping WL Elevation) |  |  |  |  | m
2. Total Pipeline Friction Losses |  |  |  |  | m
3. Total Minor Losses (fittings, bends, valves, entrance & exit) |  |  |  |  | m
4. Velocity Head at Discharge (V²/2g, last active segment) |  |  |  |  | m
TOTAL DYNAMIC HEAD (TDH) |  |  |  |  | m
SECTION 5 — PUMP REQUIREMENTS
Design Flow Rate |  |  |  |  | L/s
Total Dynamic Head (TDH) |  |  |  |  | m
Pump Efficiency η_pump |  |  |  | 0.65 | -
Motor Efficiency η_motor |  |  |  | 0.9 | -
Hydraulic Power P_hyd = ρgQH/1000 |  |  |  |  | kW
Motor / Input Power P_motor = P_hyd / (η_pump × η_motor) |  |  |  |  | kW
Daily Volume Supplied (at design flow × pump hours) |  |  |  |  | m³/day

## TRANSMISSION
TRANSMISSION MAIN PIPE SIZING — Hazen-Williams Method
HDPE PE100 ¦ Auto Pipe OD & Pressure Rating (PN) Selection ¦ Uganda WSS DM 2nd Ed.
DESIGN BASIS
Source Description (e.g. Borehole BH-1 / Production Well)
Destination Description (e.g. Service Reservoir SR-1)
Total Design Flow Q |  |  |  |  | L/s | Pump design capacity
HGL at Supply Point |  |  |  |  | m ASL | Pumped: enter pump TDH + dynamic WL elevation (from TDH_CALC). Gravity: enter reservoir HWL.
Allowable Head Loss Gradient |  |  |  |  | m/km | From PARAMETERS — override if needed
Min. Residual Head at Destination |  |  |  |  | m | From PARAMETERS — override if needed
ℹ HOW TO USE: (1) Enter segment data below — From/To Node names, Length, Elevations, and Flow Q. (2) OD and PN Rating auto-selected via AGGREGATE formula from PIPE_DB — no manual lookup needed. (3) HGL chains automatically: Segment 1 start = Supply HGL above; each subsequent start = previous end (col T). (4) BRANCHES: override HGL Start (col I) by typing =T{upstream_row} to link to the branch junction. (5) Adjust Flow Q where flow changes (e.g. at a distribution offtake). (6) Resize pipe by changing the Allowable S in the Design Basis above.
STATUS KEY: |  |  |  | ✓ OK | ⚠ LOW VELOCITY | ⚠ HIGH VELOCITY | ⚠ LOW PRESSURE | ⚠ SIZE N/A
# | From Node | To Node | Length (m) | From Elev (m ASL) | To Elev (m ASL) | ΔElev (m) | Flow Q (L/s) | HGL Start (m ASL) | Max Working Pressure (m) | Auto PN Num | Auto PN Rating | Min D_req (mm) | Auto OD (mm) | Actual ID (mm) | Velocity (m/s) | Friction hf (m) | Minor Loss (m) | Total Loss (m) | HGL End (m ASL) | Pressure at End (m) | Status
1 | [6 empty] | $E$7
2
3
4
5
6
7
8
9
10
11
12
13
14
15
TOTALS
HYDRAULIC SUMMARY
Total Pipeline Length |  |  |  |  | m
Total Friction Head Loss |  |  |  |  | m
Total Minor Head Loss |  |  |  |  | m
Total Head Loss (friction+minor) |  |  |  |  | m
HGL at Supply Point |  |  |  |  | m ASL
HGL at Destination |  |  |  |  | m ASL
Residual Head at Destination |  |  |  |  | m
Required Minimum Residual Head |  |  |  |  | m
Design Check

## DISTRIBUTION
DISTRIBUTION NETWORK PIPE SIZING — Hazen-Williams Method
HDPE PE100 ¦ Auto Pipe OD & Pressure Rating (PN) Selection ¦ Uganda WSS DM 2nd Ed.
SECTION 1 — DEMAND CALCULATION
Parameter | Value | Unit | Notes / Formula
Present Population |  | persons | Current census / community count
Design Population (auto-calculated) |  | persons | Present pop × (1 + growth rate)^design period
Per Capita Demand |  | L/cap/day | From PARAMETERS — adjust to local survey data
NRW / Loss Factor |  | - | From PARAMETERS
Peak Hour Factor (PHF) |  | - | From PARAMETERS
Gross Average Daily Demand |  | m³/day | Design pop × per_capita × NRW ÷ 1000
Average Daily Flow |  | L/s | Gross ADD × 1000 ÷ 86400
DESIGN FLOW — Peak Hour (use per branch below) |  | L/s | Average daily flow × PHF
HGL at Supply Point (Reservoir HWL) |  | m ASL | Enter reservoir high water level from TDH_CALC or survey
Min. Residual Pressure at Consumer |  | m | From PARAMETERS — Uganda WSS DM rural standard
Allowable Head Loss Gradient |  | m/km | From PARAMETERS — override if needed
ℹ BRANCHING GUIDANCE: Enter each pipe branch as one row. Set 'HGL Start' (col H) manually: • First pipe from reservoir: type =B14 (reservoir HWL). • Continuation (series): type =S{previous_row} to link to the preceding pipe's HGL End. • Branch from junction: type =S{junction_row} to link to the junction node's HGL End. Flow Q = flow carried by THAT branch only (not cumulative upstream flow). Colour coding shows hydraulic status instantly.
STATUS KEY: |  |  |  | ✓ OK | ⚠ LOW VELOCITY | ⚠ HIGH VELOCITY | ⚠ LOW PRESSURE | ⚠ SIZE N/A
# | From Node | To Node | Length (m) | From Elev (m ASL) | To Elev (m ASL) | Flow Q (L/s) | HGL Start (m ASL) [INPUT] | Max Working Pressure (m) | Auto PN Num | Auto PN Rating | Min D_req (mm) | Auto OD (mm) | Actual ID (mm) | Velocity (m/s) | Friction hf (m) | Minor Loss (m) | Total Loss (m) | HGL End (m ASL) | Pressure at End (m) | Status
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
TOTALS
SECTION 2 — NODE PRESSURE CHECK SUMMARY
Enter node names and ground elevations. In 'HGL at Node' column, type the Excel reference to the corresponding HGL End (col S) from the pipe branch table above — e.g. =S22 for the first branch end node.
# | Node Name | Ground Elev (m ASL) | HGL at Node (m ASL) [INPUT] | Pressure Head (m) | Min Required (m) | Status
1
2
3
4
5
6
7
8
9
10